| Page No./Clause | Existing Clause | Point Raised | Approved Clause |
| --- | --- | --- | --- |
| Page-5 Monitor Page-7 Monitor Page-8 Monitor Under Desktop Computer | 15.6” Wide TFT TCO Certified 17” Flat LCD Monitor 15” TFT Color MPR II complaint or TCO-03 Certified. | It was requested to change it to 18.5” LCD Monitor TCO-03 Certified because all these models (15.6”, 17” and 15”) are obsolete models and not available in the market. | The existing clauses are a amended as follows:- - 18.5” LCD Monitor TCO-03 Certified |
| Page-5 UPS | 3 KVA Line Interactive with battery Backup time Minimum 60 minutes (On Full Load) | It was requested to change the UPS Model to 3 KVA Online because 3 KVA Line Interactive UPS is not manufactured by the manufacturers. | The existing clause is deleted and new clause added as under:- 3 KVA Online with battery Backup time Minimum 60 minutes (On Full Load) - Microprocessor controlled, Double Conversion, IGBT Based with Intelligent LCD Display - Input Voltage Range – 180 to 280 AC, Single phase - Input Frequency – 47 to 53 Hz - Output Voltage – 230 +/- 2% - Output Power Rating- 2100W - Output waveform Mains mode: Same as input supply Battery mode: Sine Wave - Transfer rate –0 milliseconds - Overload protection: UPS must have all the protections at Input & Output. - Surge Suppressors: Inbuilt surge suppressor, EMI/ RFI Filters - Battery Type – Sealed Lead Acid Maintenance Free - Battery make – EXIDE, PANASONIC, Rocket & Quanta - Backup time – Minimum 60 minutes - Battery Cabinet – Batteries should be housed in a Battery Rack. - Battery quantity – 8 x 12Vx 40 AH |
| Page-8 CPU under Desktop Computer | - CPU: Intel Pentium Dual Core E2140 1.6 GHz, 1 MB L2 Cache and 800 MHz FSB with Intel EM 64 T; | The specifications of the CPU should be upgraded to 5300 instead of E2140 for better performance. | The specifications is amended as follows:- - CPU: Intel Pentium Dual Core 5300 1.6 GHz, 1 MB L2 Cache and 800 MHz FSB with Intel EM 64 T |
| Page-8 Operating System under Desktop Computer | - Windows XP Professional preloaded with media and documentation and Certificate of Authority | -- | Because Eduboss, Open Source Operating System will be utilized. The clause is deleted. |
| Page-8 Certification under Desktop Computer | Win Logo XP and Linux Certifications | -- | Because Win Logo XP and Linux Certifications are not proposed to be used. The clause is deleted. |
| Page-8 Laser Jet Printer B/W | Three years onsite warranty | As the equipment will be maintained under the maintenance contract of Phase-1 or Phase-2, onsite warranty is not needed and this clause could be deleted. | The point raised is agreed to and the clause is deleted. |
| Page-7 UPS Page-8 800 VA Line Interactive UPS | - 800 VA Interactive UPS - Output Power Capacity 360 Watts / 600 VA - Max Configurable Power 360 Watts / 600 VA - Nominal Output Voltage 120V - Nominal Input Voltage 120V - Input Frequency 60 Hz +/- 3 Hz - Input Connections NEMA 5-15P. - Cord Length 1.83 meters - Input voltage range for main operations 94 - 140V - Typical recharge time 16 hour(s) | It was requested to change the UPS specifications because these specifications never fit for 800 VA Interactive UPS. | The existing clause specifications as follows:- 800 VA Interactive UPS with following specifications - Output Power Capacity 480 Watts / 800 VA - Max Configurable Power 480 Watts / 800 VA - Nominal Output Voltage 230V AC - Nominal Input Voltage 230V AC - Input Frequency 50 Hz +/- 3 Hz - Backup Time: 30 Minutes. - Cord Length 1.50 meters Approx. - Input voltage range for main operations 140V-280V AC - Typical recharge time 8 hour(s) - Technology: PWM, Switching Device: MOSFET - Power Factor- 0.6 |

New Schedule:

Last date of submission of Bid: 30-Dec-2010 upto 2:30 PM

Date of opening of Pre Qualification Bid: 30-Dec-2010 at 3:00 PM